## Conversion
Equipment | min-cap | max-cap | efficiency | el-efficiency | th-efficiency | min-lf | ux1 | v1 | u1 | v2 | u2 | ux2 | v3 | u3 | performance-slope-1 | performance-slope-2 | IX1 | Q1 | I1 | Q2 | I2 | IX2 | Q3 | I3 | investment-slope-1 | investment-slope-2 | maint-percentage
BOI1 | 100 | 14000 | 0.9 | 1 | 1 | 0.2 | 0.0229 | 0.2 | 0.2184 | 1 | 1.0004 | 0.0229 | 1 | 1.0004 | 0.9775 | 0.9775 | 31859 | 100 | 34343 | 14000 | 379580 | 31859 | 14000 | 379580 | 24.8372 | 24.8372 | 1.5
BOI2 | 100 | 14000 | 0.9 | 1 | 1 | 0.2 | 0.0229 | 0.2 | 0.2184 | 1 | 1.0004 | 0.0229 | 1 | 1.0004 | 0.9775 | 0.9775 | 31859 | 100 | 34343 | 14000 | 379580 | 31859 | 14000 | 379580 | 24.8372 | 24.8372 | 1.5
CHP1 | 500 | 3200 | 0.87 | 0.435 | 0.434 | 0.5 | -0.0235 | 0.5 | 0.479 | 1 | 0.9815 | -0.0235 | 1 | 0.9815 | 1.005 | 1.005 | 115347 | 500 | 230022 | 712 | 278644 | 114976 | 3200 | 850563 | 229.3491 | 229.871 | 10
CHP2 | 500 | 3200 | 0.87 | 0.435 | 0.434 | 0.5 | -0.0235 | 0.5 | 0.479 | 1 | 0.9815 | -0.0235 | 1 | 0.9815 | 1.005 | 1.005 | 115347 | 500 | 230022 | 712 | 278644 | 114976 | 3200 | 850563 | 229.3491 | 229.871 | 10
AC1 | 100 | 6500 | 0.67 | 1 | 1 | 0.2 | 0.1667 | 0.2 | 0.2722 | 0.6 | 0.4833 | -0.2667 | 1 | 0.9833 | 0.52775 | 1.25 | 62385 | 50 | 68493 | 750 | 154012 | 105929 | 6500 | 522651 | 122.17 | 64.1111 | 4
AC2 | 100 | 6500 | 0.67 | 1 | 1 | 0.2 | 0.1667 | 0.2 | 0.2722 | 0.6 | 0.4833 | -0.2667 | 1 | 0.9833 | 0.52775 | 1.25 | 62385 | 50 | 68493 | 750 | 154012 | 105929 | 6500 | 522651 | 122.17 | 64.1111 | 4
TC1 | 400 | 10000 | 5.54 | 1 | 1 | 0.2 | 0.2085 | 0.2 | 0.3185 | 0.7 | 0.5936 | -0.3145 | 1 | 0.9828 | 0.5502 | 1.2973 | 27202 | 400 | 89006 | 10000 | 1572302 | 27202 | 10000 | 1572302 | 154.51 | 154.51 | 1
TC2 | 400 | 10000 | 5.54 | 1 | 1 | 0.2 | 0.2085 | 0.2 | 0.3185 | 0.7 | 0.5936 | -0.3145 | 1 | 0.9828 | 0.5502 | 1.2973 | 27202 | 400 | 89006 | 10000 | 1572302 | 27202 | 10000 | 1572302 | 154.51 | 154.51 | 1

## Demand
t | Heating | Cooling | peak-heat | peak-cool
0 | 2400 | 1200 | 4300 | 3100
1 | 1500 | 1300
2 | 700 | 2600
3 | 1500 | 1900

## ConnectivityMatrix
| BOI1 | BOI2 | CHP1 | CHP2 | AC1 | AC2 | TC1 | TC2 | HD | CD | NG | EG
BOI1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
BOI2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
CHP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
CHP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1 | 0
AC1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
TC2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
HD | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CD | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EG | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## HeatMatrix
| BOI1 | BOI2 | CHP1 | CHP2 | AC1 | AC2 | TC1 | TC2 | HD | CD | NG | EG
BOI1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BOI2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC1 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC2 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HD | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## CoolMatrix
| BOI1 | BOI2 | CHP1 | CHP2 | AC1 | AC2 | TC1 | TC2 | HD | CD | NG | EG
BOI1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BOI2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
HD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CD | 0 | 0 | 0 | 0 | 1 | 1 | 1 | 1 | 0 | 0 | 0 | 0
NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## ElectricityMatrix
| BOI1 | BOI2 | CHP1 | CHP2 | AC1 | AC2 | TC1 | TC2 | HD | CD | NG | EG
BOI1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
BOI2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CHP2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
AC2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
TC1 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
TC2 | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
HD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
CD | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
NG | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EG | 0 | 0 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Economic
gas-tariff | el-tariff | feedin-tariff | cashflow-time | discount-rate
0.06 | 0.16 | 0.1 | 10 | 0.08

## TestConversionIO
Equipment | Vector | IO
BOI | Gas | Input
BOI | Heat | Output
CHP | Gas | Input
CHP | Heat | Output
CHP | Electricity | Output
AC | Heat | Input
AC | Cool | Output
TC | Electricity | Input
TC | Cool | Output
STS | Heat | Input
STS | Heat | Output
LTS | Heat | Input
LTS | Heat | Output